## Validate
Flows | Processes | Wastes | Resources
RESOURCE | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY

## Flows
key | type
A1 | INTERNAL
A2 | INTERNAL
A3 | INTERNAL
A4 | INTERNAL
V5 | INTERNAL
V6 | INTERNAL
V7 | INTERNAL
V8 | INTERNAL
NG | RESOURCE
WC | INTERNAL
WTG | INTERNAL
WTV | INTERNAL
WP | INTERNAL
WN | OUTPUT
QG | WASTE
QC | WASTE

## Processes
key | description | fuel | product | type
COMB | Combustor | NG | A2-A1 | PRODUCTIVE
COMP | Compresor | WC | A1 | PRODUCTIVE
TGAS | Turbina Gas | A2-A3 | WTG+WC | PRODUCTIVE
HRSG | HRSG | A3-A4 | V6-V5 | PRODUCTIVE
TVAP | Turbina de vapor | V6-V7 | WTV | PRODUCTIVE
PUMP | Bomba alimentacion | WP | V5-V8 | PRODUCTIVE
ALTN | Alternador | WTG+WTV | WP+WN | PRODUCTIVE
STCK | Chimenea | A4 | QG | DISSIPATIVE
COND | Condensador | V7-V8 | QC | DISSIPATIVE

## Exergy
key | REF | GT98 | ST89 | CMP84 | ALT97 | TG1080 | PVAC8 | NET85
A1 | 52513 | 52835 | 52769 | 53517 | 53056 | 53477 | 52785 | 50193
A2 | 177657 | 178746 | 178525 | 179867 | 179495 | 179066 | 178578 | 169810
A3 | 62159 | 63406 | 62462 | 62932 | 62802 | 62282 | 62481 | 59413
A4 | 3930 | 3758 | 3949 | 3979 | 3970 | 4233 | 4051 | 3500
V5 | 362.4 | 371.2 | 364.2 | 366.9 | 366.1 | 361.3 | 388 | 280.7
V6 | 48739 | 49924 | 48977 | 49345 | 49243 | 48592 | 48991 | 45938
V7 | 4347 | 4452 | 4395 | 4428 | 4392 | 4334 | 4928 | 4310
V8 | 81 | 83 | 81.4 | 82 | 81.85 | 80.76 | 104.7 | 78.78
NG | 191241 | 192414 | 192176 | 192916 | 193220 | 192342 | 192233 | 182794
WC | 56907 | 57256 | 57185 | 58305 | 57495 | 57952 | 57202 | 54393
WTG | 51956 | 50986 | 52210 | 51912 | 52494 | 52076 | 52225 | 49661
WTV | 40197 | 41175 | 39945 | 40245 | 40613 | 40077 | 39930 | 37301
WP | 310.5 | 318.1 | 312 | 314.4 | 313.7 | 309.6 | 312.4 | 222.8
WN | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 85000
QG | 3930 | 3758 | 3949 | 3979 | 3970 | 4233 | 4051 | 3500
QC | 4266 | 4369 | 4313.6 | 4346 | 4310.15 | 4253.24 | 4823.3 | 4231.22

## Format
key | width | precision | unit
EXERGY | 11 | 1 | (kW)
EXERGY_COST | 11 | 1 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 1 | (c/h)
GENERALIZED_UNIT_COST | 10 | 4 | (c/kWh)
DIAGNOSIS | 11 | 2 | (kW)

## WasteDefinition
key | type | recycle
QG | MANUAL | 0
QC | MANUAL | 0

## WasteAllocation
key | QG | QC
COMB | 1 | 0
COMP | 0 | 0
TGAS | 0 | 0
HRSG | 0 | 1
TVAP | 0 | 0
PUMP | 0 | 0

## ResourcesCost
key | type | Base
NG | FLOW | 1.32
COMB | PROCESS | 58.8
COMP | PROCESS | 21371.4
TGAS | PROCESS | 17377.8
HRSG | PROCESS | 12220.2
TVAP | PROCESS | 2126.4
PUMP | PROCESS | 7.8
ALTN | PROCESS | 592.8
STCK | PROCESS | 6
COND | PROCESS | 314.4