## Validate
Flows | Processes | Wastes
RESOURCE | PRODUCTIVE | DEFAULT
INTERNAL | DISSIPATIVE | MANUAL
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY
HYBRID

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
B7 | INTERNAL
B8 | INTERNAL
B9 | INTERNAL
GN | RESOURCE
WTA | INTERNAL
WTB | INTERNAL
WBB | INTERNAL
WBA | INTERNAL
WN | OUTPUT
QV | OUTPUT
QC | WASTE

## Processes
key | description | fuel | product | type
BOIL | Caldera | GN | B1-B9 | PRODUCTIVE
TURA | Turbina Alta | B1-B2-B3 | WTA | PRODUCTIVE
TURB | Turbina Baja | B3-B4 | WTB | PRODUCTIVE
PUMB | Bomba Baja | WBB | B6-B5 | PRODUCTIVE
DESG | Desgasificador | B7+B6 | B8 | PRODUCTIVE
PUMA | Bomba Alta | WBA | B9-B8 | PRODUCTIVE
ALTR | Alternador | WTA+WTB | WBA+WBB+WN | PRODUCTIVE
EVAP | Evaporador | B2-B7 | QV | PRODUCTIVE
COND | Condensador | B4-B5 | QC | DISSIPATIVE

## Exergy
key | Reference | GEN97 | HP89 | LP84 | VC8 | T10
B1 | 20470 | 20602 | 20541 | 20511 | 20624 | 20498
B2 | 8606 | 8606 | 8604 | 8606 | 8606 | 8612
B3 | 3789 | 3869 | 3867 | 3814 | 3882 | 3849
B4 | 468.5 | 478.4 | 477.8 | 473.4 | 633.5 | 476.8
B5 | 7.394 | 7.549 | 7.525 | 7.442 | 13.59 | 7.566
B6 | 11.76 | 12 | 11.97 | 11.83 | 18.07 | 12.03
B7 | 1367 | 1367 | 1363 | 1367 | 1367 | 1378
B8 | 1121 | 1117 | 1114 | 1120 | 1145 | 1127
B9 | 1276 | 1273 | 1270 | 1275 | 1301 | 1284
GN | 46479 | 46824 | 46686 | 46588 | 46764 | 46661
WTA | 7549 | 7597 | 7491 | 7564 | 7605 | 7506
WTB | 2845 | 2905 | 2903 | 2830 | 2790 | 2889
WBB | 4.82 | 4.921 | 4.906 | 4.852 | 4.938 | 4.932
WBA | 180.9 | 181.9 | 181.4 | 181.2 | 182.4 | 183.1
WN | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
QV | 6945 | 6945 | 6945 | 6945 | 6945 | 6945
QC | 461.106 | 470.851 | 470.275 | 465.958 | 619.91 | 469.234

## WasteAllocation
key | QC
BOIL | 0.71542
TURA | 0.038516
TURB | 0.080113
DESG | 0.16565

## Format
key | width | precision | unit
EXERGY | 10 | 2 | (kW)
EXERGY_COST | 10 | 2 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 2 | (kW)
GENERALIZED_UNIT_COST | 10 | 4 | (J/J)
DIAGNOSIS | 10 | 3 | (kW)