## Thermodynamic Properties
Nr | E (kW) | m (kg/s) | T (ºC) | p (bar) | h (kJ/kg) | s (kJ/kg K)
0 | 0 | 242.1 | 20 | 1.013 | 0 | 0
1 | 68818 | 242.1 | 331.2 | 9.1 | 312.5 | 0.09634
2 | 203917 | 246.1 | 1000 | 9.009 | 1147 | 1.084
3 | 66513 | 246.1 | 552.2 | 1.045 | 622.7 | 1.202
4 | 6552 | 246.1 | 150.9 | 1.014 | 153.2 | 0.4317
5 | 234.8 | 35.02 | 39.31 | 42.2 | 168.3 | 0.5614
6 | 48646 | 35.02 | 510.4 | 41.37 | 3468 | 7.104
7 | 4882 | 35.02 | 39.01 | 0.07 | 2395 | 7.71
8 | 84.63 | 35.02 | 39.01 | 0.07 | 163.4 | 0.559
9 | 210706 | 3.952 | 20 | 1.013 | 53310 | 0
10 | 74441
11 | 54470
12 | 37545
13 | 174.7
14 | 90000
15 | 6552
16 | 4760

## Validate
Flows | Processes | Wastes | Resources
RESOURCE | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY

## Flows
key | type
A1 | INTERNAL
A2 | INTERNAL
A3 | INTERNAL
A4 | INTERNAL
V5 | INTERNAL
V6 | INTERNAL
V7 | INTERNAL
V8 | INTERNAL
GN | RESOURCE
WC | INTERNAL
WTG | INTERNAL
WTV | INTERNAL
WB | INTERNAL
WN | OUTPUT
QG | WASTE
QC | WASTE

## Processes
key | description | fuel | product | type
COMB | Combustor | GN | A2-A1 | PRODUCTIVE
COMP | Compresor | WC | A1 | PRODUCTIVE
TGAS | Turbina Gas | A2-A3 | WTG+WC | PRODUCTIVE
HRSG | HRSG | A3-A4 | V6-V5 | PRODUCTIVE
TVAP | Turbina de vapor | V6-V7 | WTV | PRODUCTIVE
PUMP | Bomba alimentacion | WB | V5-V8 | PRODUCTIVE
ALTN | Alternador | WTG+WTV | WB+WN | PRODUCTIVE
STCK | Chimenea | A4 | QG | DISSIPATIVE
COND | Condensador | V7-V8 | QC | DISSIPATIVE

## Exergy
key | Reference | TG1 | TV1 | ALT2 | Prueba
A1 | 71507 | 72653 | 71850 | 72247 | 68818
A2 | 216960 | 218948 | 218002 | 219207 | 203917
A3 | 69697 | 70336 | 70032 | 70419 | 66513
A4 | 7775 | 7846 | 7812 | 7855 | 6552
V5 | 438.5 | 442.6 | 440.7 | 443.1 | 234.8
V6 | 52447 | 52927 | 52699 | 52990 | 48646
V7 | 4050 | 4087 | 4096 | 4092 | 4882
V8 | 63.1 | 63.68 | 63.4 | 63.75 | 84.63
GN | 223624 | 224719 | 224698 | 225940 | 210706
WC | 77290 | 78933 | 77661 | 78091 | 74441
WTG | 61022 | 60647 | 61315 | 61654 | 54470
WTV | 41465 | 41845 | 41174 | 41894 | 37545
WB | 437.5 | 441.5 | 439.6 | 442 | 174.7
WN | 100000 | 100000 | 100000 | 100000 | 90000
QG | 7775 | 7846 | 7812 | 7855 | 6552
QC | 3986.9 | 4023.32 | 4032.6 | 4028.25 | 4760

## Format
key | width | precision | unit
EXERGY | 11 | 1 | (kW)
EXERGY_COST | 11 | 1 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 1 | (c/h)
GENERALIZED_UNIT_COST | 10 | 4 | (c/kWh)
DIAGNOSIS | 11 | 2 | (kW)

## WasteDefinition
key | type | recycle
QG | MANUAL | 0
QC | MANUAL | 0

## WasteAllocation
key | QG | QC
COMB | 1 | 0
COMP | 0 | 0
TGAS | 0 | 0
HRSG | 0 | 1
TVAP | 0 | 0
PUMP | 0 | 0

## ResourcesCost
key | type | Base
GN | FLOW | 1.32
COMB | PROCESS | 58.8
COMP | PROCESS | 21371.4
TGAS | PROCESS | 17377.8
HRSG | PROCESS | 12220.2
TVAP | PROCESS | 2126.4
PUMP | PROCESS | 7.8
ALTN | PROCESS | 592.8
COND | PROCESS | 314.4
STCK | PROCESS | 25.2