## Physical Diagram
1
2
3
4
5
6
7
8
1
3
4
5
6
9
7
8
15
10
11
13
14
13
14
12
16
2

## Validate
Flows | Processes | Wastes | Resources
RESOURCES | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCE
WASTES |  | EXERGY
COST
IRREVERSIBILITY

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
B7 | INTERNAL
B8 | INTERNAL
B9 | INTERNAL
B10 | INTERNAL
B11 | INTERNAL
B12 | INTERNAL
B13 | INTERNAL
B14 | OUTPUT
B15 | RESOURCE
B16 | WASTE

## Processes
key | description | fuel | product | type
BOIL | Boiler | B15 | (B1-B8)+(B3-B2) | PRODUCTIVE
HTRB | HP Turbine | B1-B2-B9 | B10 | PRODUCTIVE
LTRB | LP Turbine | B3-B4 | B11 | PRODUCTIVE
LPMP | LP Pump | B12 | B6-B5 | PRODUCTIVE
DRTR | Dereator | B6+B9 | B7 | PRODUCTIVE
HPMP | LP Pump | B13 | B8-B7 | PRODUCTIVE
GEN | Generator | B10+B11 | B12+B13+B14 | PRODUCTIVE
COND | Condenser | B4-B5 | B16 | DISSIPATIVE

## Exergy
key | Reference | Operation
B1 | 51121 | 49259
B2 | 35868 | 36252
B3 | 42109 | 42560
B4 | 5459 | 5517
B5 | 118.7 | 120
B6 | 218.6 | 220.9
B7 | 2359 | 1269
B8 | 2639 | 1530
B9 | 4696 | 2835
B10 | 9739 | 9384
B11 | 31517 | 31854
B12 | 115.9 | 117.2
B13 | 314.6 | 296.3
B14 | 40000 | 40000
B15 | 129713 | 130587
B16 | 5340 | 5397