## Validate
Flows | Processes | Wastes | Resources
RESOURCE | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY
HYBRID

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
QBLR | RESOURCE
WP | INTERNAL
WN | OUTPUT
QCND | WASTE

## Processes
key | fuel | product | type | description
BLR | QBLR | B1-B6 | PRODUCTIVE | Steam Generator
TRB | B1-B2 | WN+WP | PRODUCTIVE | Turbine
IHE | B2-B3 | B6-B5 | PRODUCTIVE | Internal Heat Exchanger
PMP | WP | B5-B4 | PRODUCTIVE | Pump
CND | B3-B4 | QCND | DISSIPATIVE | Condenser

## Exergy
Key | TCND30 | TCND45 | ETAT75 | PBLR15 | NoIHE | N_Butane
B1 | 81.25 | 104.4 | 86.94 | 82.39 | 81.25 | 101.3
B2 | 16.96 | 39.82 | 18.52 | 18.57 | 16.96 | 36.41
B3 | 14.93 | 36.63 | 16.01 | 16.67 | 16.96 | 34.29
B4 | 5.591 | 9.504 | 5.983 | 6.261 | 5.591 | 24.35
B5 | 7.627 | 12.05 | 8.162 | 7.917 | 7.627 | 26.83
B6 | 9.1 | 14.81 | 9.956 | 9.316 | 7.627 | 28.41
QBLR | 91.79 | 109.6 | 97.52 | 93.61 | 98.29 | 92.25
WP | 2.381 | 2.958 | 2.547 | 1.936 | 2.381 | 2.904
WN | 50 | 50 | 50 | 50 | 50 | 50
QCND | 9.339 | 27.126 | 10.027 | 10.409 | 11.369 | 9.94

## Format
key | width | precision | unit
EXERGY | 10 | 3 | (kW)
EXERGY_COST | 10 | 3 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 3 | (c/h)
GENERALIZED_UNIT_COST | 10 | 4 | (c/kWh)
DIAGNOSIS | 10 | 4 | (kW)

## WasteDefinition
flow | type | recycle
QCND | IRREVERSIBILITY | 0

## ResourcesCost
Key | Type | Base
QBLR | FLOW | 0
BLR | PROCESS | 6.5113
TRB | PROCESS | 151.7475
IHE | PROCESS | 2.5591
PMP | PROCESS | 2.1145
CND | PROCESS | 10.7467

## ExergyCND
key | TCND30 | TCND35 | TCND40 | TCND45 | TCND50
B1 | 82.99 | 89.86 | 97.69 | 106.7 | 117
B2 | 17.32 | 24.12 | 31.84 | 40.68 | 50.89
B3 | 15.25 | 21.66 | 28.98 | 37.42 | 47.23
B4 | 5.711 | 6.67 | 7.975 | 9.709 | 11.98
B5 | 7.79 | 8.91 | 10.39 | 12.31 | 14.8
B6 | 9.295 | 10.84 | 12.76 | 15.13 | 18.05
QBLR | 99.53 | 105.3 | 111.8 | 119.1 | 127.4
WP | 2.432 | 2.612 | 2.808 | 3.022 | 3.256
WN | 50 | 50 | 50 | 50 | 50
QCND | 9.539 | 14.99 | 21.005 | 27.711 | 35.25