## Physical Diagram
1
2
3
4
5
6
7
8
1
3
4
5
6
9
7
8
15
10
11
13
14
13
14
12
16
2

## Validate
Flows | Processes | Wastes | Resources
RESOURCES | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCE
WASTES |  | EXERGY
COST
IRREVERSIBILITY

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
B7 | INTERNAL
B8 | INTERNAL
B9 | INTERNAL
WT1 | INTERNAL
WT2 | INTERNAL
WP1 | INTERNAL
WP2 | INTERNAL
WN | OUTPUT
NG | RESOURCE
QC | WASTE

## Processes
key | description | fuel | product | type
BOIL | Boiler | NG | (B1-B8)+(B3-B2) | PRODUCTIVE
HTRB | HP Turbine | B1-B2-B9 | WT1 | PRODUCTIVE
LTRB | LP Turbine | B3-B4 | WT2 | PRODUCTIVE
LPMP | LP Pump | WP1 | B6-B5 | PRODUCTIVE
DRTR | Dereator | B6+B9 | B7 | PRODUCTIVE
HPMP | LP Pump | WP2 | B8-B7 | PRODUCTIVE
GEN | Generator | WT1+WT2 | WP1+WP2+WN | PRODUCTIVE
COND | Condenser | B4-B5 | QC | DISSIPATIVE

## Exergy
key | Reference | Operation
B1 | 51121 | 49259
B2 | 35868 | 36252
B3 | 42109 | 42560
B4 | 5459 | 5517
B5 | 118.7 | 120
B6 | 218.6 | 220.9
B7 | 2359 | 1269
B8 | 2639 | 1530
B9 | 4696 | 2835
WT1 | 9739 | 9384
WT2 | 31517 | 31854
WP1 | 115.9 | 117.2
WP2 | 314.6 | 296.3
WN | 40000 | 40000
NG | 129713 | 130587
QC | 5340 | 5397

## Format
key | width | precision | unit
EXERGY | 10 | 2 | (kW)
EXERGY_COST | 10 | 2 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 2 | (c/h)
GENERALIZED_UNIT_COST | 10 | 4 | (c/kWh)
DIAGNOSIS | 10 | 3 | (kW)