## Validate
Flows | Processes | Wastes | Resources
RESOURCE | PRODUCTIVE | DEFAULT | FLOW
INTERNAL | DISSIPATIVE | MANUAL | PROCESS
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY
HYBRID

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
QBLR | RESOURCE
WP | INTERNAL
WN | OUTPUT
QCND | WASTE

## Processes
key | fuel | product | type | description
BLR | QBLR | B1-B6 | PRODUCTIVE | Steam Generator
TRB | B1-B2 | WN+WP | PRODUCTIVE | Turbine
IHE | B2-B3 | B6-B5 | PRODUCTIVE | Internal Heat Exchanger
PMP | WP | B5-B4 | PRODUCTIVE | Pump
CND | B3-B4 | QCND | DISSIPATIVE | Condenser

## Exergy
key | REF | noIHE | PBLR18 | PCND2 | TRB75
B1 | 83.57 | 83.57 | 83.93 | 87.64 | 89.43
B2 | 17.9 | 17.9 | 18.46 | 21.92 | 19.54
B3 | 15.79 | 17.9 | 16.39 | 19.59 | 16.94
B4 | 5.784 | 5.784 | 6.011 | 6.34 | 6.19
B5 | 7.877 | 7.877 | 7.948 | 8.528 | 8.43
B6 | 9.42 | 7.877 | 9.471 | 10.33 | 10.31
QBLR | 100 | 106.9 | 100.8 | 103.5 | 106.3
WP | 2.447 | 2.447 | 2.264 | 2.554 | 2.619
WN | 50 | 50 | 50 | 50 | 50
QCND | 10.006 | 12.116 | 10.379 | 13.25 | 10.75

## Format
key | width | precision | unit
EXERGY | 11 | 3 | (kW)
EXERGY_COST | 11 | 3 | (kW)
EXERGY_UNIT_COST | 11 | 4 | (J/J)
GENERALIZED_COST | 11 | 3 | (c$/h)
GENERALIZED_UNIT_COST | 11 | 4 | (c$/kWh)
DIAGNOSIS | 11 | 4 | (kW)

## WasteDefinition
flow | type | recycle
QCND | IRREVERSIBILITY | 0

## ResourcesCost
Key | Type | External | Internal
QBLR | FLOW | 0.5 | 0
BLR | PROCESS | 6.51 | 6.51
TRB | PROCESS | 151.75 | 151.75
IHE | PROCESS | 2.56 | 2.56
PMP | PROCESS | 2.11 | 2.11
CND | PROCESS | 10.75 | 10.75